## IO List
HYDROELECTRIC POWER PLANT — PLC I/O LIST
TIA Portal V18 ¦ S7-1500 ¦ Revision 1.0
Signal Type | Tag Name | Device / Description | Raw Min | Raw Max | Eng. Min | Eng. Max | Eng. Units | Polarity | PLC Address | Notes
AQ | Baffle_Out | River Baffle / Control Valve (servo) | 0 | 27648 | 0 | 100 | % Open | REVERSE | QW80 | 0 raw = 100% open; 27648 raw = fully closed. Inversion handled in scaling block.
AQ | OilPumpVFDsp_Out | Oil Pump VFD — Speed Setpoint | 0 | 27648 | 0 | 100 | % | STRAIGHT | QW82 | Controls oil pump motor speed. Must also assert OilPumpVFDen_Out (DQ) to enable drive.
AI | RPM_In | Generator Rotor Speed | 0 | 27648 | 0 | 200 | RPM | STRAIGHT | IW64 | Overspeed alarm at 180 RPM (5 s delay). Brake Failure: RPM > 0 with brake engaged > 30 s.
AI | OilFlow_In | Oil Flow to Bearings | 0 | 27648 | 0 | 30 | GPM | STRAIGHT | IW66 | Low Flow alarm < 5 GPM for > 10 s (VFD on, brake off). High Flow alarm ≥ 30 GPM (5 s).
AI | OilTemp_In | Bearing Oil Temperature | 0 | 27648 | 0 | 500 | ° | STRAIGHT | IW68 | High Temp alarm at 400° (5 s delay). Warmup hold until ≥ 150°; Cooldown until < 150°.
AI | ACCurrent_In | Generator AC Output | 0 | 27648 | 0 | 700 | kW | STRAIGHT | IW70 | Overcurrent alarm at 550 kW (5 s delay). Interlock closes once stable at target kW.
DQ | Baffle_En | Baffle Enable | — | — | 0 | 1 | ON/OFF | STRAIGHT | Q0.0 | Enables baffle servo drive. De-energize in Idle and Fault.
DQ | OilPumpVFDen_Out | Oil Pump VFD — Drive Enable | — | — | 0 | 1 | ON/OFF | STRAIGHT | Q0.1 | Must be ON before VFD speed AQ has any effect. De-energize on E-Stop / Oil Low Flow / Fault.
DQ | StationInterlock_Out | Power Station Grid Interlock | — | — | 0 | 1 | ON/OFF | STRAIGHT | Q0.2 | Energize to connect generator to grid. Only close in Generation mode at stable speed.
DQ | AlarmHorn_Out | Audible Alarm Horn | — | — | 0 | 1 | ON/OFF | STRAIGHT | Q0.3 | Energize on ANY active alarm condition. Silence via HMI Alarm Silence button.
DQ | Brake_Out | Generator Rotor Mechanical Brake | — | — | 0 | 1 | ON/OFF | STRAIGHT | Q0.4 | Energize to ENGAGE brake. De-energize during Warmup–Generation. Engage in Idle/Fault/E-Stop.
DI | EStop_In | Emergency Stop (HMI button) | — | — | 0 | 1 | ON/OFF | REVERSE | I0.0 | CLOSED = normal. OPEN = E-Stop active. Immediate action — no delay. Shifts HOAs to OFF/HAND.
LEGEND
AI | Analog Input
AQ | Analog Output
DI | Digital Input
DQ | Digital Output

## Alarm Setpoints
ALARM SETPOINTS & CONFIGURATION
Alarm Name | Tag Name | Condition | Setpoint | Delay (s) | Process Action | Inhibits
Overcurrent | Alarm_Overcurrent | ACCurrent_In > setpoint | 550 kW | 5 | Disengage interlock → normal shutdown sequence | None
High Oil Temp | Alarm_HighOilTemp | OilTemp_In > setpoint | 400 ° | 5 | Disengage interlock → normal shutdown sequence | None
Rotor Overspeed | Alarm_Overspeed | RPM_In > setpoint | 180 RPM | 5 | Disengage interlock → normal shutdown sequence | None
Oil Low Flow | Alarm_OilLowFlow | OilFlow_In < setpoint (VFD on AND brake off) | 5 GPM | 10 | Disengage interlock, deenergize VFD, open baffle, engage brake | VFD inhibit
Oil High Flow | Alarm_OilHighFlow | OilFlow_In > setpoint | 30 GPM | 5 | Disengage interlock → shutdown; Override VFD to 50% of pre-fault value | None
E-Stop | Alarm_EStop | EStop_In = OPEN | — | 0 | Disengage interlock, deenergize VFD, open baffle, engage brake; HOAs → OFF / HAND | Interlock, VFD
Brake Failure | Alarm_BrakeFailure | RPM_In > 0 AND Brake_Out = 1 | — | 30 | Disengage interlock, deenergize VFD, open baffle, engage brake | None

## Scaling Reference
ANALOG SCALING REFERENCE — Raw ↔ Engineering Conversion
Tag Name | Formula (Eng → Raw) | Formula (Raw → Eng) | 0% Raw Value | 50% Raw Value | 100% Raw Value
Baffle_Out | Raw = (1 - Eng/100) × 27648 [REVERSE] | Eng = (1 - Raw/27648) × 100 | 0 | 13824 | 27648
OilPumpVFDsp_Out | Raw = (Eng/100) × 27648 | Eng = (Raw/27648) × 100 | 0 | 13824 | 27648
RPM_In | N/A (Input) | Eng = (Raw/27648) × 200 | 0 | 13824 | 27648
OilFlow_In | N/A (Input) | Eng = (Raw/27648) × 30 | 0 | 13824 | 27648
OilTemp_In | N/A (Input) | Eng = (Raw/27648) × 500 | 0 | 13824 | 27648
ACCurrent_In | N/A (Input) | Eng = (Raw/27648) × 700 | 0 | 13824 | 27648